TECHNICAL PROPOSAL

Type 1 - Standalone MCU Based FloodGuard Pilot

Central MCU with two sensor inputs, direct relay control, no RTU

| Project | Pilot Deployment of Smart Waterlogging Detection, Warning and Monitoring System |
| --- | --- |
| System Name | FloodGuard - Underpass / RUB / LHS Safety System |
| Location | To be filled by Contractor / Authority |
| Client / Authority | Nagar Nigam / Municipal Corporation / Development Authority / Railway / PWD / Smart City SPV |
| Submitted By | To be filled by Contractor |
| Date | To be filled |
| Document Version | Pilot Technical Proposal - Editable Draft |

This proposal is prepared for pilot approval. The contractor may attach commercial value on the final page without changing the technical scope, unless approved by the authority.

# 1. Objective of Pilot Project

The objective of this pilot project is to provide an automatic safety system at a waterlogging-prone underpass / RUB / LHS / low-lying road location. The system shall detect rising water level, warn public users locally, provide remote monitoring to authorised officials, and create event records for future maintenance and decision-making.

Prevent accidental entry of vehicles, two-wheelers, pedestrians and school buses into dangerous waterlogged underpass conditions.

Provide visible and audible warning at both entry/exit approaches.

Provide live site status through controller/dashboard integration as per authority requirement.

Enable future integration with automatic barrier, drain pump, traffic signal or control room system.

Generate operational records for alert time, water level, power status and system health.

# 2. Proposed System Type

| Proposal Type | Type 1 - Standalone MCU Based System |
| --- | --- |
| Architecture | Central MCU at site with two sensor inputs and direct relay/control outputs. No separate RTU is used. |
| Pilot Nature | One-site pilot, expandable to multi-site deployment after successful acceptance. |
| Primary Use Case | Urban underpass / Railway RUB / LHS / low-lying road safety and waterlogging warning. |
| Operation Mode | Automatic field operation with local warning. Remote monitoring / cloud integration can be enabled as per authority policy. |

# 3. Functional Requirements

| Sr. | Function | Requirement |
| --- | --- | --- |
| 1 | Water Level Detection | Two independent sensor inputs at MCU for water level / confirmation / redundancy as per site design. |
| 2 | Alert Levels | Configurable Normal, Orange/Warning and Danger levels in mm or equivalent threshold. |
| 3 | Local Warning | Siren, flash beacon, voice warning/display and approach-side warning devices. |
| 4 | Visual Display | P10 LED display showing live water level / warning text at approach point as per type scope. |
| 5 | CCTV Support | One CCTV camera for underpass visual verification / authority viewing as per network availability. |
| 6 | Power Backup | Solar and battery based backup for field operation as specified in the proposal type. |
| 7 | Manual Test | Authorised test for siren, flash, display and relay output during commissioning and maintenance. |
| 8 | Future Automation | Provision for barrier and drain pump automation using relay/output integration after authority approval. |
| 9 | Logs | Event logs for alert start, alert clear, maximum level and fault condition. |
| 10 | Safety Fallback | Local warning shall continue as per configuration even if remote network is unavailable. |

# 4. Design Philosophy

Fail-safe warning approach: if water reaches danger threshold, field warning should remain active until level becomes safe or authorised override is recorded.

Local-first operation: field warning does not depend only on internet or cloud connectivity.

Expandable I/O: spare relay/output capacity is reserved for future barrier, pump, traffic light or alarm integration.

Maintainable pilot design: controller, power, sensor and warning devices shall be serviceable without civil modification to main underpass structure.

Authority-friendly reporting: pilot results can be submitted as monsoon preparedness / road safety / disaster management evidence.

# 5. Type 1 System Architecture

In Type 1 architecture, one MCU panel is installed at the suitable control location near the underpass. Both sensors are connected directly to the MCU. The MCU controls local warning devices and direct relay outputs for both approach sides.

| Item | Type 1 Technical Scope |
| --- | --- |
| MCU / Controller Panel | One central MCU with two sensor inputs, relay output interface, local configuration and event logging provision. |
| Sensor Inputs | Two water level / confirmation sensor inputs connected to MCU. Final sensor mounting to be decided after site survey. |
| Relay Control | Direct relay outputs from MCU for siren, flash, display warning and future barrier/pump control. |
| RTU | Not applicable. No separate Left/Right RTU is proposed in Type 1. |
| CCTV | One CCTV camera for site visual verification. |
| Power | 60Ah LiFePO4 battery with 150W solar panel and suitable charge controller/protection. |
| Warning at Both Sides | Entry and exit side siren + flash beacon. Cable routing from MCU to both sides as per site feasibility. |
| Display | P10 LED display, 2-tile configuration, to show water level and warning message. |
| Barrier / Pump | Relay provision for future barrier automation and drain pump automation. Final interlocking to be approved separately. |

# 6. Type 1 Indicative Block Diagram

Water Sensor 1  ->  Central MCU Panel  ->  Relay Outputs  ->  Siren / Flash / P10 Display / Future Barrier / Future Pump
Water Sensor 2  ->  Central MCU Panel  ->  CCTV / Network / Local Dashboard
150W Solar Panel -> Charge Controller -> 60Ah LiFePO4 Battery -> MCU + Warning Devices

# 7. Type 1 Bill of Technical Items

| Sr. | Item | Qty. | Remarks |
| --- | --- | --- | --- |
| 1 | Central MCU controller panel | 1 set | With two sensor inputs and relay/control outputs. |
| 2 | Water level / confirmation sensors | 2 nos. | Type and mounting as per final site survey. |
| 3 | LiFePO4 battery 60Ah | 1 no. | Battery with suitable BMS/protection. |
| 4 | Solar panel 150W | 1 no. | With mounting structure and charge controller. |
| 5 | CCTV camera | 1 no. | For underpass monitoring/visual verification. |
| 6 | Siren units | 2 nos. | One at each approach side. |
| 7 | Flash beacon units | 2 nos. | One at each approach side. |
| 8 | P10 LED display | 2 tiles | For water level / warning display. |
| 9 | Relay interface / protection devices | 1 set | For output isolation, fusing and surge protection. |
| 10 | Weatherproof enclosure and accessories | 1 lot | IP-rated box, glands, terminal blocks, DIN rail, wiring. |
| 11 | Cable, conduit and mounting hardware | 1 lot | As per actual site measurement. |
| 12 | Provision for barrier and pump automation | 1 lot | Relay/output provision only; actuator/pump integration can be added separately. |

# 8. Installation and Site Work Scope

| Activity | Scope |
| --- | --- |
| Site Survey | Finalise sensor mounting height, MCU/RTU panel position, approach warning position, cable route, solar mounting location and CCTV view angle. |
| Panel Installation | Install weatherproof controller panel(s), glands, terminals, power protection, cable tagging and earthing as feasible. |
| Sensor Installation | Install two sensor inputs at approved location with mechanical protection and calibration reference. |
| Warning Device Installation | Install siren, flash beacon, display/voice warning at both approach sides as per approved drawing. |
| Power System | Install battery, solar panel / inverter / charge controller as per proposal type, with fuse and isolation provision. |
| CCTV Installation | Install one camera for underpass view and connect to available network/NVR/cloud as decided by authority. |
| Testing | Test sensor reading, alert threshold, siren, flash, display/voice, power backup, fault condition and event logging. |
| Training | Provide basic training to nominated municipal/authority staff for operation, test and report view. |

# 9. Alert and Control Logic

| Condition | System Action |
| --- | --- |
| Normal Level | Display/status shows normal. Warning outputs remain off. |
| Orange / Warning Level | Flash beacon and display/voice warning activate. Alert event is logged and notification can be sent to authorised staff. |
| Danger Level | Siren + flash + display/voice warning remain active. Optional barrier/pump output can be triggered after authority approval. |
| Water Level Clear | System returns to normal after configured safe threshold and delay. Clear event is logged. |
| Sensor Fault / Power Fault | Fault status is logged and displayed. Local warning/fallback action can be configured. |
| Manual Test | Authorised technician can test relay outputs during maintenance and commissioning. |

# 10. Dashboard / Monitoring Requirement

Site name and live alert status.

Current water level and maximum water level during event.

Sensor input status and device health.

Battery / solar / inverter status as supported by installed hardware.

CCTV view or link as per authority network policy.

Siren, flash, display/voice and future relay output status.

Event log with date, time, alert type, clear time and remarks.

PDF/Excel report export can be provided if included in final software scope.

# 11. Testing and Acceptance Criteria

System shall show sensor reading at MCU/dashboard during commissioning.

Orange and Danger threshold shall be configured and demonstrated.

Siren, flash and display/voice output shall operate as per configured alert level.

Battery/solar power operation shall be checked under available site condition.

CCTV view shall be demonstrated as per available network/NVR/cloud arrangement.

Event log shall record test alert and clear condition.

Manual test and reset/clear procedure shall be demonstrated to authority representative.

As-built wiring diagram and user handover note shall be submitted after commissioning.

# 12. Contractor Deliverables

| Deliverable | Format / Remark |
| --- | --- |
| Technical drawing | Site-specific layout showing sensor, panel, warning device, cable and solar positions. |
| Installed hardware | As per selected proposal type and approved BOQ. |
| Commissioning report | Threshold setting, test status, equipment serial/ID and site photographs. |
| Basic user training | Operation, warning response, manual test and maintenance precautions. |
| Warranty/support note | To be filled by contractor in commercial proposal. |
| Commercial proposal | One-page commercial value sheet attached at the end of this document. |

# 13. Authority / Client Responsibilities

Approval for installation location, pole/wall mounting and cable routing.

Permission for solar panel mounting and CCTV view angle.

Provision of internet/NVR/control-room access where remote monitoring/CCTV integration is required.

Approval of warning message text, siren timing, display content and alert thresholds.

Coordination with traffic police, ward office, railway/PWD/utility departments if required.

Civil foundation, trenching, road cutting, barrier civil work or pump-panel modification if not included in contractor commercial scope.

# 14. Exclusions / To Be Confirmed Before Final Order

Major civil work, drainage repair, pump replacement, dewatering pipeline work and road cutting unless specifically included in the commercial proposal.

Automatic physical boom barrier, actuator, drain pump starter modification or traffic signal integration unless separately approved.

Recurring SIM/internet charges, cloud hosting charges, NVR storage and CCTV recording charges unless commercially included.

Any statutory approvals, road closure permission or railway/PWD permission to be arranged by the authority/contractor as agreed.

Final solar sizing may require site load verification, sunlight availability and backup-hour requirement.

# 15. Pilot Outcome Expected

After successful pilot, the authority will receive practical evidence for larger deployment across vulnerable underpasses and waterlogging blackspots. The expected pilot outcomes are:

early warning before dangerous vehicle entry,

visible and audible public warning at both approaches,

operational log of waterlogging events,

better traffic and emergency response coordination,

data for future drainage, pump and barrier planning,

scalable model for city-wide monsoon preparedness.

COMMERCIAL PROPOSAL - TO BE FILLED BY CONTRACTOR

This page is intentionally provided as a one-page commercial sheet. The contractor shall fill rates, taxes, warranty and payment terms as per tender/authority requirement.

| Project / Site Name | ______________________________________________ |
| --- | --- |
| Proposal Type | ______________________________________________ |
| Contractor / Firm Name | ______________________________________________ |
| Contact Person / Mobile | ______________________________________________ |
| GST No. | ______________________________________________ |
| Validity of Offer | ________ days from date of submission |

| Sr. | Description | Qty. | Unit Rate (Rs.) | Amount (Rs.) |
| --- | --- | --- | --- | --- |
| 1 | Supply of FloodGuard hardware as per technical proposal | 1 lot |  |  |
| 2 | Installation, mounting, wiring and commissioning | 1 lot |  |  |
| 3 | Software / dashboard / monitoring setup, if applicable | 1 lot |  |  |
| 4 | Training, documentation and handover | 1 lot |  |  |
| 5 | Warranty / AMC / support, if applicable | 1 lot |  |  |
|  | Subtotal |  |  |  |
|  | GST / Taxes |  |  |  |
|  | Grand Total |  |  |  |

| Amount in Words | ________________________________________________________________________________ |
| --- | --- |
| Warranty Offered | ________________________________________________________________________________ |
| Delivery Period | ________________________________________________________________________________ |
| Payment Terms | ________________________________________________________________________________ |
| Remarks / Exclusions | ________________________________________________________________________________ |

Authorised Signatory: ______________________________        Seal: ______________________________